## Instructions
Bapco Upstream — Dispatching Solution Requirements Register v3
Purpose: | Confirm which requirements apply to Bapco Upstream.
How to use:
1. | Fill column G: Yes / No / TBD
2. | Add notes in column H
3. | YELLOW = TBD-WORKSHOP items needing input
4. | RED = marked for DISCUSSION
5. | Priority: M=Mandatory, H=Highly Desirable, D=Desirable, TBD=To be determined
Note: | Updated with Bapco Business Rules Document v2.0 (Feb 2026).
Nominations, scheduling, curtailment, quality tracking, LNG — all confirmed.

## All Requirements
# | Document | Section | Req ID | Requirement | Priority | Applicable? (Yes/No/TBD) | Workshop Notes
1 | Doc 02 - Functional Req | DISPATCHING PHILOSOPHY (FR-DP) | FR-DP-001 | The system shall support the following dispatching modes: (a) advisory/manual — system presents analysis and recommendations, dispatcher makes all decisions; (b) semi-automatic — system generates optimized dispatch schedules and setpoint recommendations that the dispatcher reviews and approves before any action. Command issuance to SCADA may be supported if SCADA-enabled, but only after explicit operator approval. | M
2 | Doc 02 - Functional Req | DISPATCHING PHILOSOPHY (FR-DP) | FR-DP-002 | The final decision authority shall rest with the dispatcher at all times. The Dispatching Solution shall NEVER autonomously issue control commands without operator approval. | M
3 | Doc 02 - Functional Req | DISPATCHING PHILOSOPHY (FR-DP) | FR-DP-003 | The system shall enforce the following hierarchy of system operations: (1) Safety first — no dispatch action may jeopardize system stability; (2) Operational reliability — maintain pressure stability, avoid supply interruptions; (3) Contractual obligations — respect customer agreements; (4) Economic efficiency — minimize cost of LNG and storage withdrawals. | M
4 | Doc 02 - Functional Req | DISPATCHING PHILOSOPHY (FR-DP) | FR-DP-004 | The system shall provide decision support during upset conditions including: supply source trips, unexpected pressure drops, demand spikes, equipment failures, and unplanned outages. The system shall present the current impact, predicted evolution, and recommended corrective actions. | M
5 | Doc 02 - Functional Req | DISPATCHING PHILOSOPHY (FR-DP) | FR-DP-005 | The system shall support 24/7 continuous dispatch operations and shall be accessible from multiple control room locations simultaneously. [TBD-WORKSHOP: Number and location of control rooms] | M
6 | Doc 02 - Functional Req | DISPATCHING PHILOSOPHY (FR-DP) | FR-DP-006 | The system shall support priority-based gas allocation during constrained supply situations using the following default hierarchy: (1) Electricity & Water Authority (EWA) plants — critical; (2) Bapco Refining & strategic industries; (3) Tier-I large industrial consumers; (4) Tier-II/III other industrial/commercial consumers. The hierarchy shall be configurable. | M
7 | Doc 02 - Functional Req | DISPATCHING PHILOSOPHY (FR-DP) | FR-DP-007 | The system shall support curtailment management with a 4-level deviation response: Level 1 — minor deviations (control adjustments); Level 2 — supply interruption risk (partial curtailment); Level 3 — network threat (load shedding in stages); Level 4 — national emergency (full authority intervention). The system shall propose curtailment scenarios for operator approval. | M
8 | Doc 02 - Functional Req | DISPATCHING PHILOSOPHY (FR-DP) | FR-DP-008 | The system shall support peak shaving and line-packing strategies: activation of storage/line-pack when required by system pressure or demand forecast; use of domestic gas (EOG) for base load; optimization of RLNG for peak conditions or economic preference. | M
9 | Doc 02 - Functional Req | DISPATCHING PHILOSOPHY (FR-DP) | FR-DP-009 | The system shall support economic dispatch considerations: cost-weighted priority dispatch if approved by management; optimization of LNG usage based on market prices and reliability requirements. | H
10 | Doc 02 - Functional Req | DISPATCHING PHILOSOPHY (FR-DP) | FR-DP-010 | Operators may override supply priority to customers with justification. All overrides shall be logged in the system and captured in the audit trail. | M
11 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-001 | The system shall perform transient (dynamic) hydraulic simulation of the pipeline network, calculating pressure, flow rate, temperature, and velocity at all points. | M
12 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-002 | The system shall perform steady-state simulation for network planning and analysis. | M
13 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-003 | The system shall support gas pipeline simulation for natural gas (domestic EOG production and regasified LNG with different compositions). | M
14 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-004 | The simulation engine shall achieve calculation accuracy within +/-1% for pressure and flow rate under steady-state conditions when compared to field measurements. | M
15 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-005 | The system shall model pipeline segments with full physical parameters (diameter, wall thickness, roughness, elevation profile, thermal properties, burial depth). | M
16 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-006 | The system shall model compressor stations with individual unit-level detail (performance curves, operating constraints, fuel consumption). [TBD-WORKSHOP: If applicable] | M
17 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-007 | The system shall model pump stations with individual pump curves and operating constraints. [TBD-WORKSHOP: If applicable] | M
18 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-008 | The system shall model pressure regulators (pressure reduction, flow limiting, back-pressure control). | M
19 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-009 | The system shall model supply sources with configurable boundary conditions (pressure, flow, composition). | M
20 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-010 | The system shall model delivery/offtake points with configurable boundary conditions. | M
21 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-011 | The system shall model storage facilities (tanks, underground storage). [TBD-WORKSHOP: If applicable] | H
22 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-012 | The system shall model network junctions, tees, and manifolds. | M
23 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-013 | The system shall model heaters and coolers with heat transfer calculations. [TBD-WORKSHOP: If applicable] | H
24 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-014 | [TBD-WORKSHOP: If compressors are present] The system shall provide compressor optimization: determination of optimum compressor and regulator operating points to minimize fuel cost / energy consumption while maintaining required delivery pressures and flows. The system shall calculate and trend compressor efficiency. | H
25 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-015 | The system shall support multi-component gas composition tracking. | M
26 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-016 | The system shall calculate derived quantities: density, viscosity, compressibility factor, heating value, Wobbe index, dew point, and speed of sound. | M
27 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-017 | The system shall support configurable unit systems (SI, imperial, and custom unit sets). | M
28 | Doc 02 - Functional Req | SIMULATION ENGINE (FR-SIM) | FR-SIM-018 | [TBD-WORKSHOP: Support for hydrogen blending or other future energy transition requirements] | D
29 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-001 | The system shall perform automatic, cyclic real-time state estimation using live SCADA data. | M
30 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-002 | The state estimation cycle time shall be configurable from 1 minute to 60 minutes. | M
31 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-003 | The state estimation shall correct sensor errors, noise, and drift in measurement data. | M
32 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-004 | The state estimation shall validate incoming SCADA data for quality. | M
33 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-005 | The system shall calculate line pack (gas) or inventory (liquid) for each pipeline segment and for the total network. The system shall classify line pack status per segment (drafting / packing / stable) and display line pack changes over configurable time periods. | M
34 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-006 | The system shall provide virtual metering capability for unmeasured or poorly measured points. | M
35 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-007 | The state estimation shall provide a model-data comparison, quantifying the residual between measured and calculated values at each measurement point. | M
36 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-008 | The state estimation shall automatically initialize from the last valid state in case of restart. | M
37 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-009 | The system shall maintain state estimation continuity during transient operations (valve switching, compressor start/stop, load changes). | M
38 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-010 | The state estimation shall employ statistical anomalous measurement detection (e.g., chi-square test on residuals) to identify instruments requiring recalibration or replacement. | H
39 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-011 | The system shall calculate mass/volume balance for configurable network zones and report imbalance trends for operational monitoring. | M
40 | Doc 02 - Functional Req | STATE ESTIMATION (FR-SE) | FR-SE-012 | The system shall support authorized operator adjustment of key measurements (e.g., correcting a known faulty reading). | H
41 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-001 | The system shall provide continuous, real-time computational pipeline monitoring (CPM) based leak detection for all monitored pipeline segments. | M
42 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-002 | The system shall generate leak alarms with configurable alarm thresholds and time delays. | M
43 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-003 | The system shall estimate the leak location (distance from reference point). | M
44 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-004 | The system shall estimate the leak rate. | M
45 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-005 | The system shall estimate the time of leak occurrence. | M
46 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-006 | The system shall minimize false alarms through statistical analysis and configurable sensitivity tuning. | M
47 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-007 | The system shall continue to provide leak detection during transient operations (within specified degraded performance). | H
48 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-008 | The system shall provide clear status indication (active, degraded, suspended) for each monitored segment. | M
49 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-009 | [TBD-WORKSHOP: Specific sensitivity requirements per pipeline segment - typically expressed as % of nominal flow rate] | M
50 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-010 | [TBD-WORKSHOP: Specific detection time requirements - typically minutes for large leaks, hours for small leaks] | M
51 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-011 | [TBD-WORKSHOP: Leak location accuracy requirements - typically +/- X km or % of segment length] | M
52 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-012 | The leak detection system shall achieve specified performance under steady-state flow conditions. Performance during transient operations shall be stated by the Contractor. | M
53 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-013 | The Contractor shall provide a leak sensitivity analysis report during commissioning demonstrating achieved performance vs. specified performance. | M
54 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-014 | Leak alarms shall include: segment ID, estimated location, estimated rate, estimated time of occurrence. | M
55 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-015 | Leak alarms shall be transmitted to the SCADA system via the defined interface. [Note: alarm acknowledgment and response remain within SCADA/operator procedures] | M
56 | Doc 02 - Functional Req | LEAK DETECTION (FR-LD) | FR-LD-016 | Leak location shall be displayed on the geographic (map) view of the pipeline network with geo-coordinates, enabling rapid identification of the physical leak site for field response. | M
57 | Doc 02 - Functional Req | PREDICTIVE ANALYSIS / LOOK-AHEAD SIMULATION (FR-PA) | FR-PA-001 | The system shall automatically and cyclically compute a prediction of future network state based on the current estimated state. | M
58 | Doc 02 - Functional Req | PREDICTIVE ANALYSIS / LOOK-AHEAD SIMULATION (FR-PA) | FR-PA-002 | The prediction horizon shall be configurable (minimum range: 1 hour to 72 hours). | M
59 | Doc 02 - Functional Req | PREDICTIVE ANALYSIS / LOOK-AHEAD SIMULATION (FR-PA) | FR-PA-003 | The prediction cycle (frequency of re-computation) shall be configurable independently from the state estimation cycle. | M
60 | Doc 02 - Functional Req | PREDICTIVE ANALYSIS / LOOK-AHEAD SIMULATION (FR-PA) | FR-PA-004 | The prediction shall use assumed future boundary conditions (supply profiles, demand profiles, control actions) which can be defined by the operator or imported from planning systems. | M
61 | Doc 02 - Functional Req | PREDICTIVE ANALYSIS / LOOK-AHEAD SIMULATION (FR-PA) | FR-PA-005 | The system shall generate early warnings for predicted violations of operational limits (overpressure, underpressure, low flow, capacity exceedance). | M
62 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-001 | The system shall allow operators and engineers to create, execute, and compare what-if scenarios without affecting the online state estimation or prediction. | M
63 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-002 | Scenarios shall be initiable from the current estimated state or from any saved state. | M
64 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-003 | The system shall support multiple concurrent scenario sessions for different users. | M
65 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-004 | Scenario modifications shall include: valve operations, compressor/pump start-stop, boundary condition changes, equipment outages, load changes, new connections. | M
66 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-005 | The system shall provide side-by-side comparison of scenario results. | M
67 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-006 | The system shall provide capacity analysis: maximum throughput under given constraints. | H
68 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-007 | The system shall provide isolation analysis: impact of isolating any section of the network. | H
69 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-008 | The system shall provide survival time analysis: time until operational limits (MAOP, minimum operating pressure) are violated after a supply interruption or other disturbance. The analysis shall consider line pack depletion rates. | H
70 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-009 | Scenarios and their results shall be saveable and reloadable. | M
71 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-010 | The system shall provide a web-based scenario interface accessible to multiple departments. | H
72 | Doc 02 - Functional Req | SCENARIO MANAGEMENT / WHAT-IF ANALYSIS (FR-SM) | FR-SM-011 | The system shall support linebreak (pipe rupture) analysis with thermal dynamics (including Joule-Thomson effects for gas), calculating pressure wave propagation, blowdown rates, and impact zone estimation. | D
73 | Doc 02 - Functional Req | OPERATOR TRAINING SIMULATOR (FR-OTS) | FR-OTS-001 | The system shall include an Operator Training Simulator using the same pipeline network model as the online system. | M | DISCUSS
74 | Doc 02 - Functional Req | OPERATOR TRAINING SIMULATOR (FR-OTS) | FR-OTS-002 | The OTS shall simulate the pipeline network in real-time or accelerated time. | M | DISCUSS
75 | Doc 02 - Functional Req | OPERATOR TRAINING SIMULATOR (FR-OTS) | FR-OTS-003 | The OTS shall support pre-defined training scenarios (normal operations, emergency procedures, fault response). | M | DISCUSS
76 | Doc 02 - Functional Req | OPERATOR TRAINING SIMULATOR (FR-OTS) | FR-OTS-004 | The OTS shall include an instructor station for initiating events, monitoring trainee actions, and controlling the simulation. | M | DISCUSS
77 | Doc 02 - Functional Req | OPERATOR TRAINING SIMULATOR (FR-OTS) | FR-OTS-005 | The instructor shall be able to introduce faults: leaks, equipment failures, sensor failures, communication failures, abnormal operating conditions. | M | DISCUSS
78 | Doc 02 - Functional Req | OPERATOR TRAINING SIMULATOR (FR-OTS) | FR-OTS-006 | The OTS shall record trainee actions and simulation results for review and evaluation. | H | DISCUSS
79 | Doc 02 - Functional Req | OPERATOR TRAINING SIMULATOR (FR-OTS) | FR-OTS-007 | The OTS shall be usable independently from the online system without interfering with live operations. | M | DISCUSS
80 | Doc 02 - Functional Req | OPERATOR TRAINING SIMULATOR (FR-OTS) | FR-OTS-008 | [TBD-WORKSHOP: Specific training scenarios required by Operations department] | M | DISCUSS
81 | Doc 02 - Functional Req | OPERATOR TRAINING SIMULATOR (FR-OTS) | FR-OTS-009 | The instructor shall have hidden controls not visible to trainees, enabling covert injection of faults and modification of simulation conditions during training exercises. | H | DISCUSS
82 | Doc 02 - Functional Req | OPERATOR TRAINING SIMULATOR (FR-OTS) | FR-OTS-010 | The OTS shall support accelerated time simulation (minimum 10x real-time) for fast-forwarding through stable periods to reach training-relevant events. | H | DISCUSS
83 | Doc 02 - Functional Req | NETWORK MODEL MANAGEMENT (FR-NM) | FR-NM-001 | The system shall provide a graphical network topology editor for creating and modifying the pipeline network model. | M
84 | Doc 02 - Functional Req | NETWORK MODEL MANAGEMENT (FR-NM) | FR-NM-002 | The graphical editor shall display the network geographically (on a map/GIS background) and schematically. | M
85 | Doc 02 - Functional Req | NETWORK MODEL MANAGEMENT (FR-NM) | FR-NM-003 | The system shall provide model version control with history tracking for all changes. | M
86 | Doc 02 - Functional Req | NETWORK MODEL MANAGEMENT (FR-NM) | FR-NM-004 | The system shall support controlled model update procedures (edit in offline mode, validate, promote to online). | M
87 | Doc 02 - Functional Req | NETWORK MODEL MANAGEMENT (FR-NM) | FR-NM-005 | The system shall support import of pipeline data from GIS systems and export to GIS. | H
88 | Doc 02 - Functional Req | NETWORK MODEL MANAGEMENT (FR-NM) | FR-NM-006 | The system shall support import of pipeline data from engineering data sources (spreadsheets, databases). | M
89 | Doc 02 - Functional Req | NETWORK MODEL MANAGEMENT (FR-NM) | FR-NM-007 | The system shall validate model integrity before deployment (connectivity checks, parameter range checks, completeness checks). | M
90 | Doc 02 - Functional Req | NETWORK MODEL MANAGEMENT (FR-NM) | FR-NM-008 | Model changes shall require appropriate authorization (role-based access control). | M
91 | Doc 02 - Functional Req | NETWORK MODEL MANAGEMENT (FR-NM) | FR-NM-009 | The system shall support multiple model instances (e.g., current operational model, development model, planning model). | H
92 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-001 | The system shall provide a GUI-based user interface for all operational and engineering functions. | M
93 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-002 | The user interface shall be web-based or provide web-based access for remote users. | H
94 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-003 | The system shall display the pipeline network graphically with color-coding of operating parameters (pressure, flow, temperature, alarms). | M
95 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-004 | The system shall provide interactive zooming, panning, and selection on network displays. | M
96 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-005 | The system shall provide time-series trend displays for any calculated or measured variable. | M
97 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-006 | The system shall provide pipeline profile displays showing pressure, flow, temperature, and elevation along a pipeline path. | M
98 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-007 | The system shall provide tabular data views with sorting and filtering. | M
99 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-008 | The system shall provide configurable dashboard layouts for different user roles (dispatcher, engineer, manager). | H
100 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-009 | The system shall support multi-screen display configurations. | M
101 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-010 | The user interface language shall be English. | M
102 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-011 | [TBD-WORKSHOP: Arabic language support requirement] | D
103 | Doc 02 - Functional Req | USER INTERFACE AND VISUALIZATION (FR-UI) | FR-UI-012 | The system shall support context-sensitive navigation (e.g., click on an alarm to navigate to the relevant network display). | H
104 | Doc 02 - Functional Req | REPORTING (FR-RP) | FR-RP-001 | The system shall generate configurable reports on pipeline network analysis results (pressure, flow, temperature, line pack, leaks). | M
105 | Doc 02 - Functional Req | REPORTING (FR-RP) | FR-RP-002 | The system shall support automated scheduled reports (daily, weekly, monthly, shift-based). | M
106 | Doc 02 - Functional Req | REPORTING (FR-RP) | FR-RP-003 | The system shall support event-triggered reports (e.g., leak alarm report). | M
107 | Doc 02 - Functional Req | REPORTING (FR-RP) | FR-RP-004 | The system shall provide scenario comparison reports. | H
108 | Doc 02 - Functional Req | REPORTING (FR-RP) | FR-RP-005 | Reports shall be exportable to PDF, Excel, and CSV formats. | M
109 | Doc 02 - Functional Req | REPORTING (FR-RP) | FR-RP-006 | The system shall support preparation of analysis reports for incident investigation. | H
110 | Doc 02 - Functional Req | REPORTING (FR-RP) | FR-RP-007 | The system shall provide the following standard reports as a minimum: Daily — dispatch report, pressure & flow summary, reconciliation report; Monthly — customer reconciliation, performance KPIs report, curtailment records. [TBD-WORKSHOP: Additional report requirements per department] | M
111 | Doc 02 - Functional Req | REPORTING (FR-RP) | FR-RP-008 | The system shall support data export for audit, regulatory, and billing purposes, including metered and calculated flow volumes, energy content, and quality data in configurable time intervals. | H
112 | Doc 02 - Functional Req | DATA MANAGEMENT (FR-DM) | FR-DM-001 | The system shall archive all state estimation results, predictions, scenario results, and alarm events. | M
113 | Doc 02 - Functional Req | DATA MANAGEMENT (FR-DM) | FR-DM-002 | The archive retention period shall be configurable (minimum 5 years recommended). | M
114 | Doc 02 - Functional Req | DATA MANAGEMENT (FR-DM) | FR-DM-003 | The system shall provide tools for querying and retrieving historical data. | M
115 | Doc 02 - Functional Req | DATA MANAGEMENT (FR-DM) | FR-DM-004 | The system shall support replay of historical states for analysis and troubleshooting. | H
116 | Doc 02 - Functional Req | DATA MANAGEMENT (FR-DM) | FR-DM-005 | The system shall provide data export capabilities for integration with external analysis tools. | M
117 | Doc 02 - Functional Req | DATA MANAGEMENT (FR-DM) | FR-DM-006 | The system shall provide automated database maintenance (backup, archiving, purging). | M
118 | Doc 02 - Functional Req | DATA MANAGEMENT (FR-DM) | FR-DM-007 | The system shall support multi-user concurrent access with data consistency and conflict prevention. | M
119 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-001 | The system shall support generation of dispatch schedules: use domestic gas (including EOG) to cover base load; optimize RLNG for peak conditions or economic preference; activate storage/line-pack only when required by system pressure or forecast. | M
120 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-002 | The dispatch schedule shall define planned operating setpoints (pressures, flows) for all controllable supply and delivery points based on nominated deliveries and supply availability. | M
121 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-003 | The system shall support demand forecasting using historical pattern matching, seasonal profiles, and optionally weather-adaptive algorithms. | H
122 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-004 | The system shall provide comparison of actual vs. scheduled operations with deviation monitoring and reporting. | M
123 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-005 | The system shall monitor received and delivered volumes at each receipt and delivery station throughout the gas day. Actual volumes shall be compared with nominated/projected volumes, and nomination imbalances shall be identified and alarmed in real time. | M
124 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-006 | The system shall support customer nominations with the following rules: (a) Day-Ahead Nomination required for all customers; (b) Hourly nominations required for major customers (if varying); (c) Intra-Day Re-Nomination allowed within contract limits; (d) Freeze Period — one hour before gas day start, no nominations accepted except emergencies. The system shall enforce these time windows. | M
125 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-007 | The system shall auto-validate nominations against annual contracted volumes and flag violations. | M
126 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-008 | The system shall perform automatic reconciliation at end of gas day: compare actual deliveries to nominations, highlight deviations (daily and cumulative), and provide imbalance reports to Gas Sales. | M
127 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-009 | The system shall support contractual penalty logic (take-or-pay) and generate billing inputs based on reconciliation data. | H
128 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-010 | The system shall track customer imbalance, generate imbalance reports, and support contractual penalty calculations. | M
129 | Doc 02 - Functional Req | DISPATCH SCHEDULING, NOMINATIONS AND DEMAND FORECAST (FR-DS) | FR-DS-011 | The system shall support configurable supply source priority order: (1) Domestic Gas/EOG (baseline); (2) RLNG (Bahrain LNG terminal); (3) Load shedding; (4) Backup inventory; (5) Future supplies. The priority order shall be operator-configurable. | M
130 | Doc 02 - Functional Req | QUALITY TRACKING (FR-QT) | FR-QT-001 | The system shall track gas composition/quality throughout the network, distinguishing between domestic gas (EOG) and RLNG sources. | M
131 | Doc 02 - Functional Req | QUALITY TRACKING (FR-QT) | FR-QT-002 | The system shall calculate quality parameters at any point (heating value, Wobbe index, specific gravity, dew points). | M
132 | Doc 02 - Functional Req | QUALITY TRACKING (FR-QT) | FR-QT-003 | The system shall predict quality at delivery points based on source compositions and network transit times. | H
133 | Doc 02 - Functional Req | QUALITY TRACKING (FR-QT) | FR-QT-004 | The system shall generate alarms for quality specification violations (predicted or actual). | M
134 | Doc 02 - Functional Req | QUALITY TRACKING (FR-QT) | FR-QT-005 | The system shall support flexible sourcing of gas composition data from: local Gas Chromatographs (GC) via SCADA, Gas Pipeline Management host system, laboratory analysis (manual entry), or a combination thereof. | M
135 | Doc 02 - Functional Req | QUALITY TRACKING (FR-QT) | FR-QT-006 | The system shall make Electronic Flow Measurement (EFM) log data available for audit and regulatory purposes. | H
136 | Doc 02 - Functional Req | PIG TRACKING (FR-PT) [IF APPLICABLE] | FR-PT-001 | The system shall track the position of pipeline pigs (inline inspection tools) in real-time using simulation and passage detector data. | TBD | TBD
137 | Doc 02 - Functional Req | PIG TRACKING (FR-PT) [IF APPLICABLE] | FR-PT-002 | The system shall predict pig arrival times at downstream stations with accuracy appropriate to pipeline length. | TBD | TBD
138 | Doc 02 - Functional Req | PIG TRACKING (FR-PT) [IF APPLICABLE] | FR-PT-003 | The system shall display pig position on the network schematic and generate alarms for pig passage at defined locations. | TBD | TBD
Doc 03 - Non-Functional
139 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-001 | The state estimation cycle shall complete within 60 seconds for the full network model. | M
140 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-002 | The look-ahead prediction (24-hour horizon) shall complete within 5 minutes. | M
141 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-003 | Steady-state analysis of the full network shall complete within 2 minutes. | M
142 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-004 | Transient analysis scenarios shall run faster than real-time (minimum 10x real-time for operator what-if scenarios). | H
143 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-005 | The system shall support a network model size of [TBD-WORKSHOP: estimated number of pipes, nodes, equipment] as a minimum. The platform shall be scalable to accommodate future network expansion of at least 50%. | M
144 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-006 | Multi-core parallel computation shall be supported to optimize calculation times. | H
145 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-007 | The system shall acquire SCADA data with a latency of no more than 5 seconds from SCADA availability. | M
146 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-008 | The system shall minimize data loss during the data integration process. Data loss shall not exceed 0.1% under normal network conditions. | M
147 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-009 | The system shall handle SCADA data rates of at least [TBD-WORKSHOP: number of measurement points] points updated every [TBD-WORKSHOP: scan rate] seconds. | M
148 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-010 | Screen refresh time for operational displays shall not exceed 3 seconds. | M
149 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-011 | Navigation between displays shall complete within 2 seconds. | M
150 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-012 | Report generation (standard reports) shall complete within 30 seconds. | H
151 | Doc 03 - Non-Functional | PERFORMANCE REQUIREMENTS | NFR-PERF-013 | Historical data retrieval for trend display (1 month of data for a single variable) shall complete within 10 seconds. | H
152 | Doc 03 - Non-Functional | AVAILABILITY AND RELIABILITY | NFR-AVL-001 | The Dispatching Solution (online components: state estimation, leak detection, prediction) shall achieve 99.5% availability, measured annually, excluding planned maintenance windows. | M
153 | Doc 03 - Non-Functional | AVAILABILITY AND RELIABILITY | NFR-AVL-002 | Planned maintenance windows shall not exceed 4 hours per month and shall be schedulable during periods of minimum operational impact. | M
154 | Doc 03 - Non-Functional | AVAILABILITY AND RELIABILITY | NFR-AVL-003 | The system shall provide redundant server architecture (primary + standby) with automatic failover. | M
155 | Doc 03 - Non-Functional | AVAILABILITY AND RELIABILITY | NFR-AVL-004 | Failover to the standby system shall complete within 5 minutes without loss of the current estimated state. | M
156 | Doc 03 - Non-Functional | AVAILABILITY AND RELIABILITY | NFR-AVL-005 | The system shall automatically restart and resume operations after a power failure, recovering from the last consistent state. | M
157 | Doc 03 - Non-Functional | AVAILABILITY AND RELIABILITY | NFR-AVL-006 | The Mean Time Between Failures (MTBF) for the complete system shall be stated by the Contractor. | M
158 | Doc 03 - Non-Functional | AVAILABILITY AND RELIABILITY | NFR-AVL-007 | The Mean Time To Repair (MTTR) for the complete system shall be stated by the Contractor. | M
159 | Doc 03 - Non-Functional | AVAILABILITY AND RELIABILITY | NFR-AVL-008 | Loss of SCADA connectivity shall not cause the Dispatching Solution to crash. The system shall operate in degraded mode using the last received data. | M
160 | Doc 03 - Non-Functional | SCALABILITY AND EXTENSIBILITY | NFR-SCL-001 | The system architecture shall support expansion of the network model (additional pipelines, stations, equipment) without re-architecture. | M
161 | Doc 03 - Non-Functional | SCALABILITY AND EXTENSIBILITY | NFR-SCL-002 | The system shall support addition of new SCADA data points without system restart. | H
162 | Doc 03 - Non-Functional | SCALABILITY AND EXTENSIBILITY | NFR-SCL-003 | The system shall support addition of new monitoring pipeline segments for leak detection. | M
163 | Doc 03 - Non-Functional | SCALABILITY AND EXTENSIBILITY | NFR-SCL-004 | The system shall be expandable with new functional modules without impacting existing functionality. | M
164 | Doc 03 - Non-Functional | SCALABILITY AND EXTENSIBILITY | NFR-SCL-005 | The system shall support concurrent access by at least [TBD-WORKSHOP: 10-20] users without performance degradation. | M
165 | Doc 03 - Non-Functional | SCALABILITY AND EXTENSIBILITY | NFR-SCL-006 | The system shall support 100% capacity expansion of the network model (doubling the number of pipeline segments, nodes, and equipment) without requiring software recompilation, redesign, or hardware replacement beyond additional compute resources. | H
166 | Doc 03 - Non-Functional | SECURITY REQUIREMENTS | NFR-SEC-001 | All user authentication shall use individual credentials (no shared accounts for operational use). | M
167 | Doc 03 - Non-Functional | SECURITY REQUIREMENTS | NFR-SEC-002 | The system shall support integration with enterprise directory services (Active Directory / LDAP). | H
168 | Doc 03 - Non-Functional | SECURITY REQUIREMENTS | NFR-SEC-003 | The system shall support encrypted communications for all network interfaces (TLS 1.2 minimum). | M
169 | Doc 03 - Non-Functional | SECURITY REQUIREMENTS | NFR-SEC-004 | The system shall comply with IEC 62443 Security Levels appropriate for the deployment zone. [TBD-WORKSHOP: Security Level target from Bapco Upstream] | M
170 | Doc 03 - Non-Functional | SECURITY REQUIREMENTS | NFR-SEC-005 | The system shall support timely application of security patches without impacting core functionality. | M
171 | Doc 03 - Non-Functional | BACKUP AND DISASTER RECOVERY | NFR-BDR-001 | The system shall support automated daily backups of configuration, model data, and archived results. | M
172 | Doc 03 - Non-Functional | BACKUP AND DISASTER RECOVERY | NFR-BDR-002 | Backup procedures shall allow for full system restoration within 4 hours. | M
173 | Doc 03 - Non-Functional | BACKUP AND DISASTER RECOVERY | NFR-BDR-003 | The system shall support configuration export/import for disaster recovery. | M
174 | Doc 03 - Non-Functional | BACKUP AND DISASTER RECOVERY | NFR-BDR-004 | The Contractor shall provide a documented backup and recovery procedure. | M
175 | Doc 03 - Non-Functional | BACKUP AND DISASTER RECOVERY | NFR-BDR-005 | Recovery Time Objective (RTO): the system shall be fully restorable from backup within [TBD-WORKSHOP: 4 hours]. | M
176 | Doc 03 - Non-Functional | BACKUP AND DISASTER RECOVERY | NFR-BDR-006 | Recovery Point Objective (RPO): maximum data loss in the event of a disaster shall not exceed [TBD-WORKSHOP: 1 hour] of operational data. | M
177 | Doc 03 - Non-Functional | BACKUP AND DISASTER RECOVERY | NFR-BDR-007 | [TBD-WORKSHOP: Disaster recovery site requirements - geographic separation, dual-site redundancy] | H
178 | Doc 03 - Non-Functional | BACKUP AND DISASTER RECOVERY | NFR-BDR-008 | DR/failover drills shall be conducted at least annually. The Contractor shall provide a DR drill procedure and participate in the first annual drill during the warranty period. | H
179 | Doc 03 - Non-Functional | MAINTAINABILITY | NFR-MNT-001 | Log levels shall be configurable (debug, info, warning, error, critical). | H
180 | Doc 03 - Non-Functional | MAINTAINABILITY | NFR-MNT-002 | Routine maintenance tasks (log rotation, database maintenance, archive management) shall be automated. | M
181 | Doc 03 - Non-Functional | MAINTAINABILITY | NFR-MNT-003 | The system shall support remote diagnostic access for the Contractor's support team (subject to Bapco Upstream security approval). | H
182 | Doc 03 - Non-Functional | MAINTAINABILITY | NFR-MNT-004 | Software updates shall be deployable without full system reinstallation. | M
183 | Doc 03 - Non-Functional | MAINTAINABILITY | NFR-MNT-005 | Configuration changes (tuning parameters, alarm thresholds, display modifications) shall be possible without software recompilation. | M
184 | Doc 03 - Non-Functional | COMPATIBILITY AND PORTABILITY | NFR-CMP-001 | The system shall run on industry-standard server hardware (x86-64 architecture). | M
185 | Doc 03 - Non-Functional | COMPATIBILITY AND PORTABILITY | NFR-CMP-002 | The Contractor shall state the supported operating systems. [PLACEHOLDER: Windows Server and/or Linux - to be aligned with Bapco Upstream IT policy] | M
186 | Doc 03 - Non-Functional | COMPATIBILITY AND PORTABILITY | NFR-CMP-003 | The system shall use industry-standard database technology. | M
187 | Doc 03 - Non-Functional | COMPATIBILITY AND PORTABILITY | NFR-CMP-004 | Client workstations shall run on standard Windows 10/11 PCs with standard web browsers. | H
188 | Doc 03 - Non-Functional | COMPATIBILITY AND PORTABILITY | NFR-CMP-005 | The system shall not require proprietary hardware that would create vendor lock-in at the infrastructure level. | M
189 | Doc 03 - Non-Functional | DATA INTEGRITY | NFR-DI-001 | The system shall maintain data consistency across all modules (simulation, state estimation, leak detection, reporting). | M
190 | Doc 03 - Non-Functional | DATA INTEGRITY | NFR-DI-002 | The system shall prevent data corruption from concurrent access. | M
191 | Doc 03 - Non-Functional | DATA INTEGRITY | NFR-DI-003 | Time synchronization across all system components shall use NTP with accuracy better than 1 second. | M
192 | Doc 03 - Non-Functional | DATA INTEGRITY | NFR-DI-004 | All archived data shall include timestamps referenced to a defined time standard (UTC or local time with timezone). | M
193 | Doc 03 - Non-Functional | DOCUMENTATION AND LOCALIZATION | NFR-DOC-001 | All documentation shall be in English. | M
194 | Doc 03 - Non-Functional | DOCUMENTATION AND LOCALIZATION | NFR-DOC-002 | User interface text shall be in English. | M
195 | Doc 03 - Non-Functional | DOCUMENTATION AND LOCALIZATION | NFR-DOC-003 | [TBD-WORKSHOP: Arabic documentation or UI localization requirement] | D
196 | Doc 03 - Non-Functional | DOCUMENTATION AND LOCALIZATION | NFR-DOC-004 | The system shall use Unicode (UTF-8) for text handling. | M
Doc 04 - Architecture
197 | Doc 04 - Architecture | NETWORK ARCHITECTURE | ARC-NET-001 | The Dispatching Solution LAN shall be physically or logically separated from the SCADA network. | M | DISCUSS
198 | Doc 04 - Architecture | NETWORK ARCHITECTURE | ARC-NET-002 | Communication between the Dispatching Solution and SCADA shall traverse a firewall/DMZ with defined, minimum-necessary rules. | M | DISCUSS
199 | Doc 04 - Architecture | NETWORK ARCHITECTURE | ARC-NET-003 | The internal LAN bandwidth shall be sufficient for all inter-component communication (minimum 1 Gbps recommended). | M | DISCUSS
200 | Doc 04 - Architecture | NETWORK ARCHITECTURE | ARC-NET-004 | Remote access to the Dispatching Solution (for web clients, remote support) shall be via approved VPN only. | M | DISCUSS
201 | Doc 04 - Architecture | NETWORK ARCHITECTURE | ARC-NET-005 | Critical servers shall be equipped with dual network interface cards (NICs) on separate network paths to provide network path redundancy. | H | DISCUSS
202 | Doc 04 - Architecture | NETWORK ARCHITECTURE | ARC-NET-006 | Network switches in the Dispatching Solution LAN shall be redundant (no single point of failure in the network path between application servers and SCADA interface). | H | DISCUSS
203 | Doc 04 - Architecture | REDUNDANCY AND FAILOVER | ARC-RED-001 | The application server shall be deployed in a primary/standby redundant configuration. | M | DISCUSS
204 | Doc 04 - Architecture | REDUNDANCY AND FAILOVER | ARC-RED-002 | The standby server shall continuously receive state synchronization from the primary server. | M | DISCUSS
205 | Doc 04 - Architecture | REDUNDANCY AND FAILOVER | ARC-RED-003 | Automatic failover shall occur if the primary server becomes unresponsive. | M | DISCUSS
206 | Doc 04 - Architecture | REDUNDANCY AND FAILOVER | ARC-RED-004 | Manual failover and failback shall be supported for maintenance purposes. | M | DISCUSS
207 | Doc 04 - Architecture | REDUNDANCY AND FAILOVER | ARC-RED-005 | The database shall be configured with replication or clustering for data protection. | M | DISCUSS
208 | Doc 04 - Architecture | REDUNDANCY AND FAILOVER | ARC-RED-006 | The system shall support operation with a single server in degraded mode if both servers are not available. | H | DISCUSS
209 | Doc 04 - Architecture | FAILURE BEHAVIOUR | ARC-FAIL-001 | Dispatching server failure: the standby server shall assume all functions within [5 minutes] without loss of state. Operators shall be notified automatically. | M | DISCUSS
210 | Doc 04 - Architecture | FAILURE BEHAVIOUR | ARC-FAIL-002 | Loss of SCADA communications: the system shall enter degraded mode, continue displaying the last known state with staleness indication, and generate an alarm. State estimation shall pause and resume automatically when communication is restored. | M | DISCUSS
211 | Doc 04 - Architecture | FAILURE BEHAVIOUR | ARC-FAIL-003 | Loss of pressure data from a station: state estimation shall continue using available data and virtual metering; affected pipeline segments shall be flagged with reduced confidence. Leak detection sensitivity for those segments shall be stated by the Contractor. | M | DISCUSS
212 | Doc 04 - Architecture | FAILURE BEHAVIOUR | ARC-FAIL-004 | Loss of communications to a single station: the system shall isolate the affected data points and continue operating on remaining data. The system shall clearly indicate which measurements are stale or missing. | M | DISCUSS
213 | Doc 04 - Architecture | FAILURE BEHAVIOUR | ARC-FAIL-005 | Database server failure: the application server shall buffer data locally and write to the database when restored. No real-time calculation data shall be lost during a database outage of up to [TBD: 4 hours]. | M | DISCUSS
214 | Doc 04 - Architecture | FAILURE BEHAVIOUR | ARC-FAIL-006 | Complete Dispatching Solution failure (both servers): the SCADA system and all safety systems shall continue to operate completely unaffected. The Dispatching Solution failure shall not degrade any other Bapco Upstream system. | M | DISCUSS
215 | Doc 04 - Architecture | TIME SYNCHRONIZATION | ARC-TIME-001 | All Dispatching Solution servers and workstations shall synchronize time via NTP to a common time source. | M | DISCUSS
216 | Doc 04 - Architecture | TIME SYNCHRONIZATION | ARC-TIME-002 | The time source shall be the same as used by the SCADA system to ensure data consistency. | M | DISCUSS
217 | Doc 04 - Architecture | TIME SYNCHRONIZATION | ARC-TIME-003 | Time synchronization accuracy shall be better than 1 second across all components. | M | DISCUSS
Doc 05 - Interfaces
218 | Doc 05 - Interfaces | GENERAL INTERFACE REQUIREMENTS | INT-GEN-001 | The system shall support industry-standard integration interfaces including OPC DA, OPC UA, OPC HDA, SQL/ODBC, REST API, and file-based exchange. | M
219 | Doc 05 - Interfaces | GENERAL INTERFACE REQUIREMENTS | INT-GEN-002 | All interfaces shall be configurable by authorized users without software recompilation. | M
220 | Doc 05 - Interfaces | GENERAL INTERFACE REQUIREMENTS | INT-GEN-003 | The Contractor shall document each interface in an Interface Design Document (IDD) specifying: protocol, data points, data formats, timing, error handling, security. | M
221 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-001 | The system shall acquire real-time process data from the SCADA system. [TBD-WORKSHOP: SCADA vendor, version, available interfaces] | M
222 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-002 | The following data types shall be acquired: analog measurements (pressure, temperature, flow rate, density), digital status (valve positions, equipment on/off), calculated values (totalized flow), gas composition data from online Gas Chromatographs (GC). | M
223 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-003 | Each data point shall include: value, quality/status flag, and timestamp. | M
224 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-004 | The interface shall support [TBD-WORKSHOP: protocol - OPC DA, OPC UA, PI SDK, database polling, ICCP]. | M
225 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-005 | The data acquisition rate shall match or exceed the SCADA scan rate. [TBD-WORKSHOP: typically 1-10 seconds] | M
226 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-006 | The system shall detect and handle stale data (data not updated within expected interval). | M
227 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-007 | Upon SCADA communication restoration, the system shall automatically resume data acquisition and re-synchronize state estimation. | M
228 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-008 | The system shall publish calculated values and leak detection results to the SCADA system for display on operator screens. | H
229 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-009 | Published data shall include: estimated pressures/flows at unmeasured points, line pack values, leak detection status and alarms, prediction summary. | H
230 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-010 | Data publication shall be READ-ONLY. The Dispatching Solution shall NEVER issue control commands to the SCADA system. | M
231 | Doc 05 - Interfaces | SCADA INTERFACE (PRIMARY) | INT-SCADA-011 | [TBD-WORKSHOP: Protocol for publishing results back to SCADA] | H
232 | Doc 05 - Interfaces | HISTORIAN INTERFACE | INT-HIST-001 | The system shall interface with the existing process data historian for access to historical measurement data. [TBD-WORKSHOP: Historian vendor - OSIsoft PI, Honeywell PHD, Wonderware, etc.] | H
233 | Doc 05 - Interfaces | HISTORIAN INTERFACE | INT-HIST-002 | Historical data retrieval shall be used for: offline analysis, replay of historical events, training scenario preparation. | H
234 | Doc 05 - Interfaces | HISTORIAN INTERFACE | INT-HIST-003 | The system shall optionally write its calculated results (state estimation, predictions, leak detection outputs) to the historian for long-term archiving. | D
235 | Doc 05 - Interfaces | HISTORIAN INTERFACE | INT-HIST-004 | [TBD-WORKSHOP: Historian interface protocol - PI SDK, OPC HDA, SQL, REST API] | H
236 | Doc 05 - Interfaces | ERP INTERFACE | INT-ERP-001 | [TBD-WORKSHOP: Determine if ERP integration is required and what data is exchanged] | TBD | TBD
237 | Doc 05 - Interfaces | ERP INTERFACE | INT-ERP-002 | Potential data from ERP: production schedules, delivery nominations, product specifications, maintenance schedules. | TBD | TBD
238 | Doc 05 - Interfaces | ERP INTERFACE | INT-ERP-003 | Potential data to ERP: actual throughput summaries, line pack reports, operational KPIs. | TBD | TBD
239 | Doc 05 - Interfaces | ERP INTERFACE | INT-ERP-004 | [TBD-WORKSHOP: ERP system identity - SAP, Oracle, etc.] | TBD | TBD
240 | Doc 05 - Interfaces | GIS INTERFACE | INT-GIS-001 | The system shall support import of pipeline geographic data from GIS for model construction and display. | H
241 | Doc 05 - Interfaces | GIS INTERFACE | INT-GIS-002 | Supported GIS data formats shall include: [TBD-WORKSHOP: Shapefile, GeoJSON, WMS/WFS, database] | H
242 | Doc 05 - Interfaces | GIS INTERFACE | INT-GIS-003 | The system shall be capable of generating model data from GIS pipeline spatial information (coordinates, elevation, routing). | H
243 | Doc 05 - Interfaces | GIS INTERFACE | INT-GIS-004 | The system shall support export of pipeline model data to GIS. | D
244 | Doc 05 - Interfaces | GIS INTERFACE | INT-GIS-005 | [TBD-WORKSHOP: GIS system identity - ArcGIS, QGIS, etc.] | H
245 | Doc 05 - Interfaces | CUSTOMER NOMINATION PORTAL INTERFACE | INT-CP-001 | The system shall interface with a cloud-based customer nomination portal for receiving day-ahead nominations, intra-day re-nominations, and nomination updates. | M
246 | Doc 05 - Interfaces | CUSTOMER NOMINATION PORTAL INTERFACE | INT-CP-002 | The system shall publish to the portal: delivery point status, actual delivered volumes, quality at delivery, nomination compliance status. | H
247 | Doc 05 - Interfaces | CUSTOMER NOMINATION PORTAL INTERFACE | INT-CP-003 | [TBD-WORKSHOP: Portal technology — existing portal to integrate with, or new portal to be specified?] | M
248 | Doc 05 - Interfaces | CUSTOMER NOMINATION PORTAL INTERFACE | INT-CP-004 | The system shall enforce nomination time windows (freeze period, re-nomination limits) as defined in the dispatch rules. | M
249 | Doc 05 - Interfaces | LNG TERMINAL INTERFACE | INT-LNG-001 | The system shall interface with the Bahrain LNG terminal systems. | M
250 | Doc 05 - Interfaces | LNG TERMINAL INTERFACE | INT-LNG-002 | Data from LNG terminal: send-out rates, LNG/regasified gas composition, tank levels, regasification capacity. | M
251 | Doc 05 - Interfaces | LNG TERMINAL INTERFACE | INT-LNG-003 | Data to LNG terminal: predicted pipeline conditions at terminal connection, requested send-out schedule. | H
252 | Doc 05 - Interfaces | LNG TERMINAL INTERFACE | INT-LNG-004 | The system shall access LNG cargo scheduling data: cargo ETA, regas capacity availability, terminal maintenance windows. | M
253 | Doc 05 - Interfaces | LNG TERMINAL INTERFACE | INT-LNG-005 | [TBD-WORKSHOP: LNG terminal system vendor and interface protocol] | M
254 | Doc 05 - Interfaces | WEATHER DATA INTERFACE | INT-WX-001 | The system shall support import of weather data (ambient temperature, wind speed, solar radiation) for thermal simulation. | D
255 | Doc 05 - Interfaces | WEATHER DATA INTERFACE | INT-WX-002 | Weather data may be acquired via: automated weather station feed, meteorological service API, or manual entry. | D
256 | Doc 05 - Interfaces | WEATHER DATA INTERFACE | INT-WX-003 | [TBD-WORKSHOP: Available weather data sources in Bahrain] | D
257 | Doc 05 - Interfaces | FIELD SYSTEM INTERFACE CLARIFICATION | INT-FS-001 | The Dispatching Solution shall NOT interface directly with PLCs, RTUs, or flow computers. All field data acquisition is via the SCADA system. | M
258 | Doc 05 - Interfaces | FIELD SYSTEM INTERFACE CLARIFICATION | INT-FS-002 | The Contractor shall state all communication protocols supported for SCADA integration (OPC DA, OPC UA, OPC HDA, Modbus TCP, ICCP/TASE.2, PI SDK, database polling, REST API, etc.). | M
259 | Doc 05 - Interfaces | FIELD SYSTEM INTERFACE CLARIFICATION | INT-FS-003 | Interface responsibility matrix: the Contractor is responsible for the Dispatching Solution side of all interfaces; Bapco Upstream (or its SCADA integrator) is responsible for the source system side. A joint interface coordination procedure shall be established during detailed design. | M
260 | Doc 05 - Interfaces | INTERFACE TESTING REQUIREMENTS | INT-TEST-001 | Each interface shall be individually tested during FAT using simulated data. | M
261 | Doc 05 - Interfaces | INTERFACE TESTING REQUIREMENTS | INT-TEST-002 | Each interface shall be tested end-to-end during SAT with live systems. | M
262 | Doc 05 - Interfaces | INTERFACE TESTING REQUIREMENTS | INT-TEST-003 | Interface failure modes shall be tested: communication loss, data corruption, buffer overflow, timeout. | M
263 | Doc 05 - Interfaces | INTERFACE TESTING REQUIREMENTS | INT-TEST-004 | The Contractor shall provide interface test procedures as part of the test documentation. | M
Doc 06 - Cybersecurity
264 | Doc 06 - Cybersecurity | GENERAL CYBERSECURITY REQUIREMENTS | CYB-GEN-001 | The Dispatching Solution shall comply with IEC 62443 (Industrial Automation and Control Systems Security). | M
265 | Doc 06 - Cybersecurity | GENERAL CYBERSECURITY REQUIREMENTS | CYB-GEN-002 | The Contractor shall demonstrate organizational compliance with ISO 27001 (Information Security Management System) or provide evidence of equivalent information security practices. | H
266 | Doc 06 - Cybersecurity | GENERAL CYBERSECURITY REQUIREMENTS | CYB-GEN-003 | The Contractor shall comply with Bapco Upstream's Information Security policies. [TBD-WORKSHOP: Obtain specific policies] | M
267 | Doc 06 - Cybersecurity | GENERAL CYBERSECURITY REQUIREMENTS | CYB-SL-001 | The target Security Level (per IEC 62443-3-3) for the Dispatching Solution zone shall be [TBD-WORKSHOP: SL-2 or SL-3 based on Bapco risk assessment]. | M
268 | Doc 06 - Cybersecurity | GENERAL CYBERSECURITY REQUIREMENTS | CYB-SL-002 | The Contractor shall demonstrate compliance with the target Security Level through a Security Level matrix. | M
269 | Doc 06 - Cybersecurity | ACCESS CONTROL | CYB-AC-001 | Each user shall have a unique individual account. Shared/generic accounts are prohibited for operational use. | M
270 | Doc 06 - Cybersecurity | ACCESS CONTROL | CYB-AC-002 | Automatic session timeout after configurable idle period (default 30 minutes). | M
271 | Doc 06 - Cybersecurity | ACCESS CONTROL | CYB-AC-003 | The system shall support integration with Active Directory / LDAP for centralized authentication. | H
272 | Doc 06 - Cybersecurity | NETWORK SECURITY | CYB-NET-001 | The Dispatching Solution shall reside in a dedicated network zone (VLAN) separated from the SCADA process network. | M
273 | Doc 06 - Cybersecurity | NETWORK SECURITY | CYB-NET-002 | All communication between the Dispatching Solution and SCADA shall pass through a firewall with explicit allow rules (default deny). | M
274 | Doc 06 - Cybersecurity | NETWORK SECURITY | CYB-NET-003 | A DMZ shall be implemented for any communication between the Dispatching Solution (OT) and enterprise/IT networks. | M
275 | Doc 06 - Cybersecurity | NETWORK SECURITY | CYB-NET-004 | All external-facing interfaces shall use encrypted communication (TLS 1.2 or higher). | M
276 | Doc 06 - Cybersecurity | NETWORK SECURITY | CYB-NET-005 | Remote access (for vendor support, remote users) shall be via approved VPN with MFA only. | M
277 | Doc 06 - Cybersecurity | NETWORK SECURITY | CYB-NET-006 | All network ports shall be documented. Only required ports shall be open; all others shall be blocked. | M
278 | Doc 06 - Cybersecurity | NETWORK SECURITY | CYB-NET-007 | The system shall not require direct internet access for operational functionality. | M
279 | Doc 06 - Cybersecurity | SYSTEM HARDENING | CYB-HRD-001 | All unnecessary services, ports, and protocols shall be disabled on all system components. | M
280 | Doc 06 - Cybersecurity | SYSTEM HARDENING | CYB-HRD-002 | Default vendor accounts and passwords shall be changed or disabled before deployment. | M
281 | Doc 06 - Cybersecurity | SYSTEM HARDENING | CYB-HRD-003 | The operating system shall be hardened according to CIS Benchmarks or equivalent. | H
282 | Doc 06 - Cybersecurity | SYSTEM HARDENING | CYB-HRD-004 | Application whitelisting shall be supported on operational servers. | H
283 | Doc 06 - Cybersecurity | SYSTEM HARDENING | CYB-HRD-005 | Anti-virus / endpoint protection shall be compatible with the Dispatching Solution. The Contractor shall certify compatibility with [TBD-WORKSHOP: Bapco's AV solution]. | M
284 | Doc 06 - Cybersecurity | PATCH MANAGEMENT | CYB-PAT-001 | Critical security patches shall be evaluated and a recommendation provided within 30 days of publication. | M
285 | Doc 06 - Cybersecurity | PATCH MANAGEMENT | CYB-PAT-002 | OS and third-party software patches shall be tested for compatibility with the Dispatching Solution before deployment. | M
286 | Doc 06 - Cybersecurity | PATCH MANAGEMENT | CYB-PAT-003 | The Contractor shall certify compatibility with Bapco Upstream's standard patch cycle. | M
287 | Doc 06 - Cybersecurity | DATA PROTECTION | CYB-DP-001 | Sensitive configuration data (passwords, API keys, certificates) shall be stored encrypted. | M
288 | Doc 06 - Cybersecurity | DATA PROTECTION | CYB-DP-002 | Data at rest (database, archive) encryption shall be supported. [TBD-WORKSHOP: Required or optional] | H
289 | Doc 06 - Cybersecurity | DATA PROTECTION | CYB-DP-003 | Data in transit between system components shall use encrypted protocols. | M
290 | Doc 06 - Cybersecurity | DATA PROTECTION | CYB-DP-004 | Backup media shall be encrypted. | H
291 | Doc 06 - Cybersecurity | SUPPLY CHAIN SECURITY | CYB-SC-001 | The Contractor shall have a vulnerability disclosure and response process. | M
292 | Doc 06 - Cybersecurity | SUPPLY CHAIN SECURITY | CYB-SC-002 | The Contractor shall notify Bapco Upstream of any discovered vulnerabilities in the Dispatching Solution or its components within 48 hours. | M
293 | Doc 06 - Cybersecurity | SUPPLY CHAIN SECURITY | CYB-SC-003 | [TBD-WORKSHOP: Any restrictions on country of origin for software components] | TBD | TBD
294 | Doc 06 - Cybersecurity | SUPPLY CHAIN SECURITY | CYB-SC-004 | The Contractor's obligation to notify Bapco Upstream of newly discovered security vulnerabilities in the Dispatching Solution shall not expire with the warranty period. This obligation shall remain in effect for as long as the Dispatching Solution is in operational use and the Contractor continues to operate as a commercial entity. | H
295 | Doc 06 - Cybersecurity | SUPPLY CHAIN SECURITY | CYB-SC-005 | The Contractor shall provide source code for all custom-developed interface modules (SCADA interface, historian interface, etc.) together with build instructions, enabling Bapco Upstream to independently maintain integration components. | H
296 | Doc 06 - Cybersecurity | INCIDENT RESPONSE | CYB-IR-001 | The Contractor shall support Bapco Upstream's incident response process for cybersecurity events affecting the Dispatching Solution. | M
297 | Doc 06 - Cybersecurity | INCIDENT RESPONSE | CYB-IR-002 | The Contractor shall provide forensic support capabilities for investigating security incidents. | H
298 | Doc 06 - Cybersecurity | INCIDENT RESPONSE | CYB-IR-003 | The system shall support isolation from external networks without losing core offline functionality. | H
Doc 07 - HW/SW
299 | Doc 07 - HW/SW | GENERAL REQUIREMENTS | HW-GEN-001 | The Contractor shall provide detailed hardware and software specifications for the complete Dispatching Solution. | M
300 | Doc 07 - HW/SW | GENERAL REQUIREMENTS | HW-GEN-002 | All hardware shall be enterprise-grade, suitable for 24/7 continuous operation in an industrial control room environment. | M
301 | Doc 07 - HW/SW | GENERAL REQUIREMENTS | HW-GEN-003 | All hardware shall be from established, internationally supported manufacturers. | M
302 | Doc 07 - HW/SW | GENERAL REQUIREMENTS | HW-GEN-004 | Hardware shall be current-generation at time of delivery; end-of-life products are not acceptable. | M
303 | Doc 07 - HW/SW | GENERAL REQUIREMENTS | HW-GEN-005 | Spare parts availability shall be guaranteed for a minimum of 7 years from delivery. | H
304 | Doc 07 - HW/SW | GENERAL REQUIREMENTS | HW-GEN-006 | [TBD-WORKSHOP: Determine whether hardware is supplied by Contractor or by Bapco Upstream to Contractor specifications] | M
305 | Doc 07 - HW/SW | GENERAL REQUIREMENTS | HW-GEN-007 | All servers shall be dimensioned at the operational system performance required plus a minimum of 35% spare capacity (CPU, RAM, disk I/O) to accommodate future expansion and peak load conditions. The Contractor shall provide a supporting sizing calculation for review and approval. | M
306 | Doc 07 - HW/SW | GENERAL REQUIREMENTS | HW-GEN-008 | All servers and critical network equipment shall be equipped with dual redundant hot-swappable power supplies connected to separate power feeds (or UPS circuits). | M
307 | Doc 07 - HW/SW | GENERAL REQUIREMENTS | HW-GEN-009 | All servers and workstations shall be rack-mountable in standard 19" racks. | M
308 | Doc 07 - HW/SW | GENERAL REQUIREMENTS | HW-GEN-010 | The proposed hardware configuration shall be expandable by adding CPU, memory, or disk units without replacing the base platform. | H
309 | Doc 07 - HW/SW | NETWORK EQUIPMENT | HW-NET-001 | Managed Ethernet switches for the Dispatching Solution LAN (minimum 1 Gbps). | M
310 | Doc 07 - HW/SW | NETWORK EQUIPMENT | HW-NET-002 | Industrial-grade firewall for SCADA/Dispatching Solution boundary. [TBD-WORKSHOP: or use existing Bapco firewall infrastructure] | M
311 | Doc 07 - HW/SW | NETWORK EQUIPMENT | HW-NET-003 | All network equipment shall support SNMP for monitoring. | H
312 | Doc 07 - HW/SW | NETWORK EQUIPMENT | HW-NET-004 | Network cabling: Cat6A or better for copper; fiber where required for distance/isolation. | M
313 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-OS-001 | Server operating system: [TBD-WORKSHOP: Windows Server 2022 or later / Linux Enterprise]. The Contractor shall state supported OS versions. | M
314 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-OS-002 | Workstation operating system: [TBD-WORKSHOP: Windows 10/11 Professional or Enterprise]. | M
315 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-OS-003 | All OS licenses required for the Dispatching Solution shall be included in the scope of supply. | M
316 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-APP-001 | The Contractor shall provide all application software licenses for the Dispatching Solution modules. | M
317 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-APP-002 | License type shall be perpetual (not subscription-based) for the operational system. [TBD-WORKSHOP: Licensing model preference] | M
318 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-APP-003 | The license shall cover the specified number of concurrent users without per-user licensing restrictions. | M
319 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-APP-004 | The Contractor shall state all third-party software dependencies and their licensing requirements. | M
320 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-APP-005 | Software version and release notes shall be maintained and provided with each update. | M
321 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-ADD-001 | Office productivity software (if required for reporting): Microsoft Office or compatible. | D
322 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-ADD-002 | PDF viewer for report viewing. | M
323 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-ADD-003 | Web browser (latest versions of Chrome, Edge, or Firefox) for web-based client access. | M
324 | Doc 07 - HW/SW | SOFTWARE REQUIREMENTS | SW-ADD-004 | Anti-virus / endpoint protection compatible with the Dispatching Solution. | M
Doc 08 - Testing
325 | Doc 08 - Testing | TESTING STRATEGY OVERVIEW | TST-DOC-001 | The Contractor shall prepare and submit a Master Test Plan (MTP) covering all test phases. | M
326 | Doc 08 - Testing | TESTING STRATEGY OVERVIEW | TST-DOC-002 | The Contractor shall prepare detailed test procedures for each test phase, submitted for Bapco Upstream review minimum 4 weeks before each test. | M
327 | Doc 08 - Testing | TESTING STRATEGY OVERVIEW | TST-DOC-003 | Test procedures shall include: test case ID, test objective, prerequisites, test steps, expected results, pass/fail criteria. | M
328 | Doc 08 - Testing | TESTING STRATEGY OVERVIEW | TST-DOC-004 | Test results shall be documented in formal test reports, signed by both parties. | M
329 | Doc 08 - Testing | TESTING STRATEGY OVERVIEW | TST-DOC-005 | A punch list / snag list shall be maintained for all test phases, with classification (critical, major, minor) and resolution tracking. | M
330 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-001 | The FAT shall demonstrate all functional requirements defined in Document 02. | M
331 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-002 | The FAT shall use the Bapco Upstream network model (or a representative subset if the full model is not available). | M
332 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-003 | The FAT shall use simulated SCADA data (pre-recorded datasets or data generators). | M
333 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-004 | The FAT shall test all user roles and access control. | M
334 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-005 | The FAT shall demonstrate reporting capabilities. | M
335 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-006 | The FAT shall test system backup and restore procedures. | M
336 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-007 | Bapco Upstream personnel shall witness the FAT. Travel and accommodation for Bapco witnesses is Bapco Upstream's responsibility. | M
337 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-008 | All critical and major test cases shall pass. | M
338 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-009 | No critical punch items shall remain unresolved. | M
339 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-010 | A plan for resolution of remaining major and minor punch items shall be agreed. | M
340 | Doc 08 - Testing | FACTORY ACCEPTANCE TEST (FAT) | TST-FAT-011 | FAT acceptance does not relieve the Contractor of obligations for SAT performance. | M
341 | Doc 08 - Testing | INTEGRATED FACTORY ACCEPTANCE TEST (iFAT) | TST-IFAT-001 | The iFAT shall test data acquisition from simulated or replayed SCADA data through the actual SCADA interface protocol. | M
342 | Doc 08 - Testing | INTEGRATED FACTORY ACCEPTANCE TEST (iFAT) | TST-IFAT-002 | The iFAT shall replay historical SCADA data representing: normal operations, transient events (valve switching, load changes), abnormal conditions, data quality issues (missing data, stale data). | M
343 | Doc 08 - Testing | INTEGRATED FACTORY ACCEPTANCE TEST (iFAT) | TST-IFAT-003 | The iFAT shall test the complete state estimation -> leak detection -> prediction chain with realistic data. | M
344 | Doc 08 - Testing | INTEGRATED FACTORY ACCEPTANCE TEST (iFAT) | TST-IFAT-004 | The iFAT shall inject simulated leak scenarios into the replayed data and verify leak detection performance. | M
345 | Doc 08 - Testing | INTEGRATED FACTORY ACCEPTANCE TEST (iFAT) | TST-IFAT-005 | The iFAT shall test SCADA communication failure and recovery behavior. | M
346 | Doc 08 - Testing | INTEGRATED FACTORY ACCEPTANCE TEST (iFAT) | TST-IFAT-006 | The iFAT shall test failover from primary to standby server. | M
347 | Doc 08 - Testing | INTEGRATED FACTORY ACCEPTANCE TEST (iFAT) | TST-IFAT-007 | [TBD-WORKSHOP: Determine if other external interfaces can be tested in iFAT - historian, GIS, etc.] | H
348 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-001 | The SAT shall verify all functional requirements with live SCADA data. | M
349 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-002 | The SAT shall verify state estimation accuracy: residuals between measured and calculated values shall be within specified tolerances. | M
350 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-003 | The SAT shall verify leak detection system is operational on all monitored segments. | M
351 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-004 | The SAT shall verify all external interfaces are operational (SCADA, historian, GIS, etc. as applicable). | M
352 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-005 | The SAT shall verify system redundancy and failover with live data. | M
353 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-006 | The SAT shall include an operator usability review by Bapco Upstream operations personnel. | H
354 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-007 | The SAT shall verify backup and disaster recovery procedures at the production site. | M
355 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-008 | All critical and major test cases shall pass. | M
356 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-009 | State estimation accuracy shall meet specified tolerances for a minimum continuous period of 72 hours. | M
357 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-010 | Leak detection shall be demonstrated operational (status active, no false alarms) for a minimum continuous period of 72 hours. | M
358 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-011 | No critical punch items shall remain unresolved. | M
359 | Doc 08 - Testing | SITE ACCEPTANCE TEST (SAT) | TST-SAT-012 | All training shall be completed before SAT sign-off. | M
360 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-ACC-001 | Steady-state simulation accuracy: calculated pressures shall be within +/-1% of measured values at all measurement points under steady-state conditions. | M
361 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-ACC-002 | Steady-state simulation accuracy: calculated flow rates shall be within +/-2% of measured values. | M
362 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-ACC-003 | State estimation residuals shall be within defined tolerances for all measurement categories. | M
363 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-ACC-004 | Line pack / inventory calculation accuracy shall be within [TBD-WORKSHOP: +/-2%] of independently verified values. | M
364 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-ACC-005 | Prediction accuracy (D+1): predicted pressures and flows shall be within [TBD-WORKSHOP: +/-1-3%] under stable conditions. | H
365 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-LD-001 | The Contractor shall perform a leak sensitivity analysis for each monitored pipeline segment. | M
366 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-LD-002 | The sensitivity analysis shall determine: minimum detectable leak size, detection time, location accuracy, and false alarm rate for each segment. | M
367 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-LD-003 | Leak detection performance shall be verified against the specified requirements. [TBD-WORKSHOP: Specific targets per segment] | M
368 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-LD-004 | [PLACEHOLDER: If safe to do, a controlled leak test or gas withdrawal test may be performed during commissioning to validate leak detection in the field] | D
369 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-LD-005 | Model tuning shall be performed iteratively until specified leak detection performance is achieved. Model accuracy and leak detection performance shall be contractual warranty items. | M
370 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-END-001 | The system shall complete a Provisional Operation Period (POP) / endurance test of continuous unattended operation for a minimum of [TBD: 30-60 consecutive days]. | M
371 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-END-002 | During the endurance test: state estimation shall run within defined accuracy, leak detection shall be active with zero false alarms, no system crashes or restarts (other than planned). | M
372 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-END-003 | System availability during the endurance test shall meet or exceed the specified availability target. | M
373 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-END-004 | Any unplanned system downtime exceeding [TBD: 12] hours during the POP shall reset the endurance test clock, and the consecutive-day count restarts from zero. | M
374 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-END-005 | Final acceptance and warranty start shall be conditional upon successful completion of the POP. | M
375 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-END-006 | The Contractor shall provide on-call support during the entire POP period, with response times per the warranty SLA. | M
376 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-DR-001 | The SAT shall include a complete failover drill: simulated primary server failure, automatic failover to standby, verification of continuous operation, and manual failback. | M
377 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-DR-002 | The SAT shall include a backup and restore test: complete system restore from backup media and verification of correct operation with restored configuration and data. | M
378 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-PAR-001 | [TBD-WORKSHOP: If existing dispatching/monitoring systems exist] The Dispatching Solution shall support a parallel operation period where it reads SCADA data simultaneously with any existing system without interference ("data eavesdropping mode"). | H
379 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-PAR-002 | During parallel operation, the Dispatching Solution results shall be compared against the existing system results and field measurements to build confidence before full operational handover. | H
380 | Doc 08 - Testing | PERFORMANCE AND ACCURACY TESTING | TST-PAR-003 | The parallel operation period shall last a minimum of [TBD: 2-4 weeks] before the existing system is decommissioned. | H
Doc 09 - Training
381 | Doc 09 - Training | TRAINING PROGRAMS | TRN-001-001 | System Overview and Concepts | All stakeholders
382 | Doc 09 - Training | TRAINING PROGRAMS | TRN-002-001 | Operator Training - Basic Operations | Dispatchers / Control Room Operators
383 | Doc 09 - Training | TRAINING PROGRAMS | TRN-003-001 | Operator Training - Advanced Analysis | Senior Operators, Shift Supervisors
384 | Doc 09 - Training | TRAINING PROGRAMS | TRN-004-001 | Leak Detection Operations | Operators, Pipeline Integrity Engineers
385 | Doc 09 - Training | TRAINING PROGRAMS | TRN-005-001 | Scenario Management and Planning | Planning Engineers, Operations Engineers
386 | Doc 09 - Training | TRAINING PROGRAMS | TRN-006-001 | Network Model Maintenance | Model Engineers
387 | Doc 09 - Training | TRAINING PROGRAMS | TRN-007-001 | System Administration | IT/OT Support Staff
388 | Doc 09 - Training | TRAINING PROGRAMS | TRN-008-001 | OTS Instructor Training | Training Instructors | DISCUSS
389 | Doc 09 - Training | TRAINING PROGRAMS | TRN-009-001 | Train-the-Trainer | Selected power users
390 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-001 | Training shall be delivered by qualified instructors with operational experience in pipeline dispatching solutions. | M
391 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-002 | Training shall be conducted in English. | M
392 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-003 | Training shall combine classroom instruction with hands-on practical exercises. Minimum 50% hands-on for operator courses. | M
393 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-004 | Training shall use the actual Bapco Upstream network model and realistic data. | M
394 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-005 | Maximum class size: 8 participants for hands-on courses, 20 for overview course. | H
395 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-006 | The Contractor shall provide the following training materials: participant manuals, instructor guides, hands-on exercise books, quick reference cards. | M
396 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-007 | All training materials shall be provided in electronic format (PDF minimum) and [TBD: printed copies]. | M
397 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-008 | Training completion certificates shall be issued to all participants. | H
398 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-009 | The Contractor shall accommodate repeat sessions if Bapco Upstream operates shift patterns requiring multiple training runs. [TBD-WORKSHOP: Number of shift groups] | M
399 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-010 | [TBD-WORKSHOP: Training to be delivered at Bapco site, at Contractor's facility, or both] | M
400 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-011 | Bapco Upstream shall have the right to video-record all training sessions for internal knowledge retention and future reference. Recordings shall remain Bapco Upstream's property and shall not be distributed externally. | H
401 | Doc 09 - Training | TRAINING REQUIREMENTS | TRN-REQ-012 | [TBD-WORKSHOP: Training-in-residence option] The Contractor shall offer the option for [TBD: 1-3] Bapco Upstream staff to be embedded at the Contractor's premises during the implementation phase for knowledge transfer and hands-on participation in model construction and system configuration. | D
402 | Doc 09 - Training | CHANGE MANAGEMENT | CM-001-001 | The Contractor shall support Bapco Upstream's change management process for the introduction of the Dispatching Solution. | H
403 | Doc 09 - Training | CHANGE MANAGEMENT | CM-002-001 | The Contractor shall provide a Change Impact Assessment identifying affected workflows, roles, and procedures. | H
404 | Doc 09 - Training | CHANGE MANAGEMENT | CM-003-001 | The Contractor shall participate in stakeholder communication sessions as required. | H
405 | Doc 09 - Training | CHANGE MANAGEMENT | CM-004-001 | The Contractor shall provide operational procedure templates for the Dispatching Solution integration into Bapco Upstream's operational workflows. | H
406 | Doc 09 - Training | CHANGE MANAGEMENT | CM-005-001 | [TBD-WORKSHOP: Specific change management requirements from Bapco Upstream HR/Operations] | TBD | TBD
407 | Doc 09 - Training | CHANGE MANAGEMENT | CM-010-001 | The Contractor shall provide on-site go-live support for a minimum of [TBD: 2-4 weeks] after SAT acceptance. | M
408 | Doc 09 - Training | CHANGE MANAGEMENT | CM-011-001 | Go-live support shall include: system monitoring, troubleshooting, on-the-job coaching, model fine-tuning. | M
409 | Doc 09 - Training | CHANGE MANAGEMENT | CM-012-001 | Go-live support shall cover all operational shifts. | M

## Summary
Document | Count | M | H | D | TBD
Doc 02 - Functional Req | 138 | 105 | 27 | 3 | 3
Doc 03 - Non-Functional | 58 | 45 | 12 | 1 | 0
Doc 04 - Architecture | 21 | 18 | 3 | 0 | 0
Doc 05 - Interfaces | 46 | 25 | 12 | 5 | 4
Doc 06 - Cybersecurity | 35 | 24 | 10 | 0 | 1
Doc 07 - HW/SW | 26 | 22 | 3 | 1 | 0
Doc 08 - Testing | 56 | 49 | 6 | 1 | 0
Doc 09 - Training | 29 | 11 | 7 | 1 | 1
TOTAL | 409